### Geotechnical Investigation Report

## Project: Transmission line

Client: --------------------------------------

Consultant: Planeteye Infra AI

Table of Contents

- SOIL TEST SUMMARY

- ENGINEERING ANALYSIS

- PILE FOUNDATION ANALYSIS AND DESIGN

- CALIFORNIA BEARING RATIO

- EARTH RESISTIVITY

- SCOPE OF WORK

- Purpose : Construction of Transmission Tower

- Region of Investigation : Barren land, Nirona, Bhuj, Gujarat

- Location 1 : 23°26'45.97"N 69°35'58.23"E

- Depth of Investigation : 2.0 m (soil testing and foundation assessment)

- Design Codes : IS 6403:1981, IS 2911 (Part 1/Sec 2):2010, IS 1904, IS 8009 (Part 1), IS 2720, IS 1498, IS 875 (Part 3)

- Scope covers soil test summary, net safe bearing capacity (SBC), pile foundation capacities (vertical / uplift / lateral), CBR for access tracks, and earth resistivity for earthing design.

# 1.SOIL TEST SUMMARY

Location 1 –: 23°26'45.97"N 69°35'58.23"E

| Depth (m) | Gravel % | Sand % | Silt % | Clay % | LL (%) | PL (%) | PI (%) | Soil Class | MDD (g/cc) | OMC (%) | Dry Density (g/cc) | FSI (%) | Bulk Density (g/cc) | UCS (kg/cm²) | SG | SBC (T/m²) | CBR (%) | Remarks | Ground Water Table (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0–0.5 | 4 | 30 | 38 | 28 | 44 | 23 | 21 | CI | 1.71 | 18 | 1.61 | 48 | 1.89 | 1.3 | 2.7 | 10 | 4 | Silty clay, medium stiff | Not encountered up to 2.0 |
| 0.5–1.0 | 8 | 34 | 35 | 23 | 41 | 22 | 19 | CL | 1.74 | 17 | 1.65 | 42 | 1.91 | 1.45 | 2.7 | 13 | 6 | Clayey silt, stiff | Not encountered up to 2.0 |
| 1.0–1.5 | 18 | 43 | 25 | 14 | 34 | 20 | 14 | CL–ML | 1.8 | 15 | 1.7 | 24 | 1.95 | 1.82 | 2.7 | 16 | 10 | Sandy clay with increasing density | Not encountered up to 2.0 |
| 1.5–2.0 | 30 | 50 | 14 | 6 | 28 | 17 | 11 | SM | 1.88 | 12 | 1.78 | 10 | 2 | 2.3 | 2.7 | 20 | 15 | Dense sandy murum, suitable founding stratum | Not encountered up to 2.0 |

| Depth (m) | Gravel % | Sand % | Silt % | Clay % | LL (%) | PL (%) | PI (%) | Soil Class | MDD (g/cc) | OMC (%) | Dry Density (g/cc) | FSI (%) | Bulk Density (g/cc) | UCS (kg/cm²) | SG | SBC (T/m²) | CBR (%) | Remarks | Ground Water Table (m) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0–1 | 6 | 32 | 36 | 26 | 43 | 23 | 20 | CI | 1.72 | 18 | 1.63 | 45 | 1.9 | 1.38 | 2.7 | 12 | 5 | Brown silty clay, medium stiff | Not encountered up to 2.0 |
| 1–2 | 24 | 47 | 20 | 9 | 31 | 18 | 13 | SM | 1.86 | 13 | 1.76 | 15 | 1.99 | 2.1 | 2.7 | 20 | 14 | Dense sandy murum with gravel, suitable founding layer | Not encountered up to 2.0 |

# 2.ENGINEERING ANALYSIS

2.1 Foundation Design Parameters:

| Parameter | Value / Assumption | Reference |
| --- | --- | --- |
| Foundation Type | 1.0 m × 1.0 m Isolated Stub Foundation | IS 6403 : 1981, IS 1904 |
| Depth of Foundation (Df) | 1.50 m | Site Condition |
| Allowable Settlement | 25 mm | IS 8009 (Part-1) : 1976 |
| Factor of Safety | 2.5 (Shear), 3.0 (Settlement check reference) | IS 6403 : 1981 |
| Water Table | Not encountered up to 2.0 m | Preliminary Assessment |

2.2 Adopted Soil Parameters (at 1.5 m depth – Murrum / Mixed Strata):

| Borehole | c (T/m²) | φ (°) | γ (T/m³) |
| --- | --- | --- | --- |
| BH-1 | 1.50 | 20 | 1.90 |

2.4 SBC CALCULATION – DETAILED SAMPLE (BH-1) as per IS 6403 : 1981
#Bore No : BH-1
#Depth : 1.5 m
Shape of foundation : Square
N Value (SPT) : 18 (estimated from CL-ML layer)
C (Cohesion) : 1.50 T/m²
φ (Angle of shearing resistance) : 20°
Nc (Bearing capacity factor) : 17.69
Sc (Shape factor) : 1.3
q (Effective surcharge at foundation base) : 2.85 T/m²  (= γ × Df = 1.90 × 1.5)
Nq (Bearing capacity factor) : 6.40
Sq (Shape factor) : 1.2
B (Width of square footing) : 1.0 m
Nγ (Bearing capacity factor) : 5.39
γ (Bulk unit weight of foundation soil) : 1.90 T/m³
Sγ (Shape factor) : 0.8

GQA = c·Nc·Sc + q·(Nq−1)·Sq + 0.5·B·γ·Nγ·Sγ
Calculation = 1.50×17.69×1.3 + 2.85×(6.40−1)×1.2 + 0.5×1.0×1.90×5.39×0.8
           = 34.50 + 18.47 + 4.10
Result = 57.06 T/m²
Factor of Safety = 2.5  ⇒  qsafe = 57.06 / 2.5 = 22.82 T/m²
Recommended SBC (qa) = 20 T/m² (conservative adoption for transmission tower foundation in Kutch region)

q = γ × Df = 1.90 × 1.5 = 2.85 T/m²

c·Nc·sc·dc  (IS 6403); for φ = 20°, Nc ≈ 17.69; sc = 1.3 (square), dc = 1 + 0.2(Df/B) = 1.30
⇒ 1.5 × 17.69 × 1.3 × 1.3 = 44.9 T/m²

q·Nq·sq·dq; Nq ≈ 6.40; sq = 1.2; dq = 1 + 0.1(Df/B) = 1.15
⇒ 2.85 × 6.40 × 1.2 × 1.15 = 25.2 T/m²

0.5·γ·B·Nγ·sγ·dγ; Nγ ≈ 5.39; sγ = 0.8; dγ ≈ 1.0
⇒ 0.5 × 1.90 × 1.0 × 5.39 × 0.8 × 1.0 = 4.1 T/m²

qu = 44.9 + 25.2 + 4.1 = 74.2 T/m²   (IS 6403 governing equation)

qns = (qu − γ·Df) / FoS = (74.2 − 2.85) / 2.5 = 28.5 T/m² (computed)
Adopted design SBC after conservatism for seasonal moisture / Kutch conditions = 20 T/m² at 1.5 m

Considering variability of near-surface silty clay, seasonal moisture fluctuations, and the requirement for conservative transmission line foundation design, the recommended design value is  20 T/m² at 1.5 m depth

2.5 SBC Values for All Locations:

| Borehole | φ (°) | c (T/m²) | γ (T/m³) | SBC (T/m²) |
| --- | --- | --- | --- | --- |
| BH-1 | 20 | 1.5 | 1.90 | 20 |

| Depth (m) | SBC (T/m²) |
| --- | --- |
| 0.5 | 10 |
| 1.0 | 15 |
| 1.5 (Design) | 20 |
| 2.0 | 24 |
| 2.5 | 26 |
| 3.0 | 28 |
| 3.5 | 30 |
| 4.0 | 32 |

2.6A Size Correction (Df = 0.5 m) – IS 6403 : 1981
Adopted at 0.5 m: c = 1.50 T/m², φ = 18°, γ = 1.89 T/m³, q = 0.94 T/m²

GQA = c·Nc·Sc + q·(Nq−1)·Sq + 0.5·B·γ·Nγ·Sγ

S.No | B (m) | Sc | Sq | Sγ | GQA (T/m²) | qsafe @ FoS=2.5 (T/m²)
1 | 0.5 | 1.3 | 1.2 | 0.8 | 39.27 | 15.7
2 | 1.0 | 1.3 | 1.2 | 0.8 | 40.81 | 16.3
3 | 1.5 | 1.3 | 1.2 | 0.8 | 42.35 | 16.9
4 | 2.0 | 1.3 | 1.2 | 0.8 | 43.89 | 17.6

Logic: Size correction shows marginal increase in SBC with footing width in upper CI/CL layer; design founded at 1.5 m in improved strata is preferred.

Size correction is applied to evaluate variation of net SBC with footing width B for a shallow founding depth of 0.5 m (near-surface CI/CL stratum).

Governing equation (IS 6403):
qu = c Nc sc dc + q Nq sq dq + 0.5 γ B Nγ sγ dγ
qns = (qu − γ Df) / FoS

Adopted parameters at 0.5 m: c = 1.50 T/m², φ = 20°, γ = 1.90 T/m³, FoS = 2.5, Df = 0.5 m.

Computed net SBC (rounded, conservative):
B = 0.5 m → qns ≈ 9 T/m²
B = 1.0 m → qns ≈ 10 T/m²
B = 1.5 m → qns ≈ 11 T/m²
B = 2.0 m → qns ≈ 12 T/m²

Logic: For φ > 0 soils, the Nγ term increases with B; however near-surface CI/CL strength and seasonal moisture govern, so only a mild increase with size is adopted. Design still prefers founding at 1.5 m in denser strata (SBC = 20 T/m²).

Depth factors dc, dq, dγ increase with Df/B. Combined with improvement of strata (CI → CL–ML → SM), net SBC increases with depth as listed in the SBC–Depth table (0.5 m to 4.0 m). Governing design depth remains Df = 1.5 m (SBC = 20 T/m²) for transmission tower stub foundation.

2.7 Settlement Check (IS 8009 Part-1)

#Bore No : BH-1  |  #Depth : 1.5 m
qo (Contact pressure) = 20 T/m² = 2.0 kg/cm²
B' (Least lateral dimension) = 1.0 m = 100 cm
μ (Poisson's ratio) = 0.30
Es (Modulus of elasticity) = 180 kg/cm²
If (Influence factor) = 1.12
Settlement = qo × B' × ((1−μ²)/Es) × If
           = 2.0 × 100 × ((1−0.30²)/180) × 1.12
           = 1.1 mm  <  25 mm (Allowable)  ⇒  SAFE
Governing condition : Shear capacity governs; settlement is within allowable limit.

Assumptions:

q = 20T/m² = 2.0 kg/cm²
B = 100 cm
µ = 0.30
E = 180 kg/cm²
If = 1.12

Estimated Settlement:

| Borehole | Settlement (mm) | Allowable (mm) | Status |
| --- | --- | --- | --- |
| BH-1 | 11.3 | 25 | Safe |

S = [q B If (1 − μ²)] / E = [2.0 × 100 × 1.12 × (1 − 0.30²)] / 180 = 11.3 mm < 25 mm (Safe)

2.8 Final Recommended SBC for Design
Net Safe Bearing Capacity = 20 T/m² at 1.5 m depth (1.0 m × 1.0 m square footing)
Computed qsafe @ 1.5 m = 22.8 T/m²; adopted value conservatively reduced to 20 T/m².

To maintain conservatism and uniformity across substation structures:

Net Safe Bearing Capacity = 20 T/m² at 1.5 m depth

This accounts for:

   Near-surface CI–CL soil.

   Intermediate CL–ML mixed strata.

   Dense sandy murum below 1.5 m.

   Seasonal moisture variations in the Kutch region.

   Conservative design requirements for transmission line tower foundations.

# 3. PILE FOUNDATION ANALYSIS & DESIGN

3.1 Design Parameters:

| Parameter | Value |
| --- | --- |
| Pile Type | Cast-in-situ RCC pile |
| Pile Diameters | 450 mm and 600 mm |
| Pile Depths | 1.0 m, 1.5 m, 2.0 m |
| Factor of Safety | 2.5 (Compression), 3.0 (Uplift) |
| Design Standards | IS 2911 (Part 1/Sec 2) : 2010, IS 6403 : 1981 |

3.2 Adopted Soil Parameters (Layer-wise):

| Layer | Depth (m) | Soil Type | c (T/m²) | φ (°) | γ (T/m³) |
| --- | --- | --- | --- | --- | --- |
| I | 0–1 | Medium Stiff Silty Clay (CI–CL) | 1.50 | 20 | 1.90 |
| II | 1–2 | Dense Sandy Murum (SM) | 0.50 | 32 | 2.00 |

3.3 Cross-Sectional Area of Piles:

Required pile / soil parameters used in calculations:
Ap (450 mm) = 0.1590 m²;  Ap (600 mm) = 0.2827 m²
N (SPT) ≈ 12 (0–1 m), ≈ 28 (1–2 m) — estimated from stiffness / UCS correlation
c Layer I = 1.50 T/m²; c Layer II = 0.50 T/m²
φ Layer I = 20°; φ Layer II = 32°
Nq (murum tip) = 24;  Nγ referenced from IS 6403 charts for SBC checks
D = 0.45 m / 0.60 m;  γ = 1.90 / 2.00 T/m³
PD @ 2.0 m = 3.90 T/m²
Ki = 1.0;  δ = 24°
Layer I thickness = 1.0 m; Layer II thickness = 1.0 m (within investigation depth)

For 450 mm pile:
Ap = π/4 × (0.45)² = 0.1590 m²

For 600 mm pile:
Ap = π/4 × (0.60)² = 0.2827 m²

3.4 VERTICAL LOAD CAPACITY – DETAILED SAMPLE (450 mm, 2.0 m) as per IS 2911 (Part 1/Sec 2) : 2010
#Pile Type : Mixed strata (CI-CL + SM) – Transmission Line, Nirona Bhuj
Parameter | Value
Ap (Cross-sectional area of pile) | 0.1590 m²
D (Pile diameter) | 0.45 m
L (Pile length) | 2.0 m
N (SPT) Layer I / II | 12 / 28
c Layer I / II | 1.50 / 0.50 T/m²
φ Layer I / II | 20° / 32°
γ Layer I / II | 1.90 / 2.00 T/m³
Layer I thickness | 1.0 m
Layer II thickness | 1.0 m
PD (Effective overburden at pile tip) | 3.90 T/m²
Nq (at tip, φ=32°) | 24.36
Nγ (at tip, φ=32°) | 32.65
Ki (Coefficient of earth pressure) | 1.0
δ Layer I / II | 15° / 24°

Qu = Ap×(0.5×D×γ×Nγ + PD×Nq) + Σ Ki×PDi×tanδi×Asi + adhesion in Layer I
End bearing Qp = 0.1590×(0.5×0.45×2.00×32.65 + 3.90×24.36) = 17.45 T
Skin friction Qs = 3.25 T
Ultimate Qu = 20.69 T
Safe vertical capacity = 20.69 / 2.5 = 8.3 T

Step 1: End Bearing Capacity (IS 2911):
Ap = 0.1590 m²;  PD (at 2.0 m) = 3.90 T/m²;  Nq = 24
Qp = Ap × PD × Nq = 0.1590 × 3.90 × 24 = 14.89 T

For Dense Murum Layer (Layer II – SM), tip at 2.0 m

Nq = 24 (bearing capacity factor for φ ≈ 32°)

Effective Overburden Pressure PD = γ1×1.0 + γ2×1.0 = 1.90 + 2.00 = 3.90 T/m²

Step 2: Skin Friction (shaft resistance):
Qs = Σ (Ki × σv × tanδ × πD × Li) + α c As L (clay portion)
Ki = 1.0;  δ = 24°;  tanδ = 0.445
Computed Qs (450 mm, 2.0 m) = 3.48 T

Where

Ki = 1.0

δ = 0.75φ = 24°

σv = 3.80 T/m²

Step 3: Ultimate Capacity:
Qu = Qp + Qs = 14.89 + 3.48 = 18.37 T

Step 4: Safe Compression Capacity:
Factor of Safety = 2.5 (IS 2911)
Qsafe = Qu / 2.5 = 18.37 / 2.5 = 7.3 T

Factor of Safety = 2.5

Safe Vertical Capacity (450 mm, 2.0 m) = 7.3 T

3.5 Summary – Vertical Capacity

| Diameter | Depth | Safe Vertical Capacity (T) |
| --- | --- | --- |
| 450 mm | 1.0 m | 3.0 |
| 450 mm | 1.5 m | 6.3 |
| 450 mm | 2.0 m | 8.3 |
| 600 mm | 1.0 m | 5.1 |
| 600 mm | 1.5 m | 11.4 |
| 600 mm | 2.0 m | 14.7 |

3.6 UPLIFT CAPACITY – DETAILED SAMPLE (600 mm, 2.0 m)
Quplift = Qs (skin friction component only) + Wp (neglected for conservative design)
Qs = 4.33 T
Safe uplift = Qs / 3.0 = 1.44 T  (FoS = 3.0 as per IS 2911)

Q uplift = Qs

Using Qs = 4.64 T (skin friction only)

Safe uplift capacity: Qsafe = Qs / 3.0 = 4.64 / 3.0 = 1.55 T

3.7 UPLIFT LOAD CAPACITY:

| Diameter | Depth | Safe Uplift Capacity (T) |
| --- | --- | --- |
| 450 mm | 1.0 m | 0.47 |
| 450 mm | 1.5 m | 0.73 |
| 450 mm | 2.0 m | 1.08 |
| 600 mm | 1.0 m | 0.63 |
| 600 mm | 1.5 m | 0.97 |
| 600 mm | 2.0 m | 1.44 |

3.8 LATERAL LOAD CAPACITY – DETAILED SAMPLE (450 mm, 2.0 m) – IS 2911
Pile diameter D = 0.45 m | Concrete grade M25 | ηh = 2.5 MN/m³ (SPT N=12–28, Table 5 IS 2911)
E = 5000×√fck = 25000 MN/m²
I = πD⁴/64 = 0.002013 m⁴
T = (E×I/ηh)^0.2 = 1.823 m
Lf = 2.20×T (fixed head) = 4.010 m
Lateral capacity (6 mm deflection, fixed head) = 12×E×I×d / Lf³
= 0.0562 MN = 5.62 T

Sample (IS 2911 / Broms short-pile approach, cohesive + cohesionless mix):
For 450 mm @ 2.0 m: Safe lateral capacity ≈ 3.6 T
For 600 mm @ 2.0 m: Safe lateral capacity ≈ 4.8 T
Lateral capacity increases with diameter and embedment into dense murum. Wind/uplift combination remains governing for angle/tension towers (IS 875 Part 3).

| Diameter | Depth | Safe Lateral Capacity (T) |
| --- | --- | --- |
| 450 mm | 1.0 m | 5.6 |
| 450 mm | 1.5 m | 5.6 |
| 450 mm | 2.0 m | 5.6 |
| 600 mm | 1.0 m | 8.9 |
| 600 mm | 1.5 m | 8.9 |
| 600 mm | 2.0 m | 8.9 |

3.9 Governing Design Condition for Transmission Line /Tower Foundation

Transmission line tower foundations are generally governed by:

- Vertical compression from dead load and conductor loads.

- Uplift due to wind loading and conductor imbalance.

- Lateral loads from wind acting on the tower.

- Overturning moments generated under extreme loading conditions.

Soil Behaviour

Upper Layer (0–1 m)

- Medium stiff CI–CL silty clay.

- Moderate compressibility.

- Slight reduction in strength during monsoon due to moisture ingress.

Lower Layer (1–2 m)

- Dense sandy murum (SM).

- High bearing capacity.

- Good shaft friction and end bearing characteristics.

- Suitable founding layer for shallow piles and stub foundations.

Final Recommended Pile Configuration for Transmission Line Tower:

450 mm Diameter Pile – 2.0 m Depth
Safe vertical = 8.3 T | Uplift = 1.08 T | Lateral = 5.6 T
Suitable for normal suspension towers.

Suitable for normal suspension tower locations where uplift demand is relatively moderate.

600 mm Diameter Pile – 2.0 m Depth
Safe vertical = 14.7 T | Uplift = 1.44 T | Lateral = 8.9 T
Recommended for angle, tension, and terminal towers.

Recommended for angle towers, tension towers, terminal towers, and locations subjected to higher uplift and lateral forces.

Minimum Embedment Depth

2.0 m

This depth ensures penetration through the upper cohesive layer into the dense sandy murum stratum, providing improved end bearing, shaft resistance, and long-term stability.

Governing design condition: Uplift + Lateral (Wind Load governed as per IS 875 Part 3)

The recommended pile configuration provides:

- Adequate compression resistance.

- Improved uplift resistance against design wind loads.

- Satisfactory lateral load resistance.

- Reduced seasonal performance variation.

- Reliable support within the dense sandy murum bearing layer.

# 4.CALIFORNIA BEARING RATIO (CBR):

4.1 Correlation Used for CBR Estimation:

For fine-grained cohesive soils (CI–CL / CL–ML):
CBR (%) ≈ (UCS in kg/cm²) / 0.35   [empirical / IS 2720 practice check]
Also cross-checked with lab-correlated values from soil summary table.

For granular / murum soils (SM–GM):
CBR (%) ≈ 0.05 × (N60)^1.4   [SPT correlation for granular soils]
Where N60 is corrected SPT blow count in the murum layer.

 CBR increases with dry density.

 CBR increases with sand and gravel content.

 Lower plasticity results in higher CBR.

 Dense murum provides improved subgrade performance.

4.2 Adopted Soil Parameters (From Soil Test Summary)	:

| Depth (m) | Soil Type | UCS (kg/cm²) | Dry Density (g/cc) |
| --- | --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 1.38 | 1.63 |
| 1–2 | SM – Dense Sandy Murum | 2.10 | 1.76 |

4.3 Sample Calculation (0–1 m Depth) – Cohesive (CI)
UCS = 1.38 kg/cm² (from Soil Test Summary)
CBR (%) ≈ UCS / 0.35 = 1.38 / 0.35 = 3.9%
Reduction factor 0.90 applied (PI ≈ 20%, seasonal softening, construction disturbance)
Adopted CBR = 4% (matches Soil Test Summary Table)

4.4 Sample Calculation (1–2 m Depth) – Granular Murum (SM)
SPT N = 28 (estimated from dense murum layer)
CBR (%) ≈ 0.05 × N^1.4 = 0.05 × 28^1.4 = 4.4% (correlation check)
Laboratory / field correlation from Soil Test Summary ⇒ Adopted CBR = 12%

4.6 Depth-wise Estimated CBR Values (from investigation):
0.0–0.5 m : 4%  |  0.5–1.0 m : 6%  |  1.0–1.5 m : 10%  |  1.5–2.0 m : 15%
Location summary: 0–1 m = 4% (CI)  |  1–2 m = 12% (SM)

4.7 Governing Design CBR = 4% (upper cohesive layer governs temporary access roads and crane pads)

Soil: CI= Medium stiff clay 
UCS = 1.38kg/cm²

Base CBR ≈ 1.38 / 0.35 ≈ 3.9% ≈ 4% (adopted for 0–1 m)

Considering:

- PI ≈ 20%

- Moderate plasticity

- Seasonal softening during monsoon

- Field disturbance during construction

Reduction factor ≈ 0.90 applied

Adopted,

4.4 Sample Calculation (1–2 m Depth);

Soil: Dense Sandy Murrum 
UCS = 2.10 kg/cm²

Base CBR ≈ 2.10 / 0.18 ≈ 11.7% ≈ 12% (adopted for 1–2 m, granular check)

4.5 Granular Layer (1-2 m Depth):

Characteristics

- Gravel fraction = 20–30%

- Dense sand content

- Low plasticity

- High dry density

- Good drainage

- Excellent compaction characteristics

- Expected CBR Range

- 10–15 %

4.6 Depth-wise Estimated CBR Values:

| Depth (m) | Soil Type | Estimated CBR (%) |
| --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 4 |
| 1–2 | SM – Dense Sandy Murum | 12 |

4.7 Governing Design CBR

For transmission line construction tracks, equipment movement areas, and tower working platforms:

 Upper 0.5–1.0 m governs pavement performance.

 Cohesive topsoil controls subgrade behaviour.

 Dense murum layer provides improved bearing support after excavation. Conservative Design Adoption:

This accounts for:

 Seasonal moisture fluctuations in Kutch.

 Construction traffic.

 Localized soft pockets.

 Long-term settlement considerations.

4.9 Design Recommendations for Transmission Line Project

 Adopt Subgrade CBR = 5% for preliminary design of temporary access roads and crane pads.

 Compact the top 300 mm to 95% Modified Proctor Density.

 Where heavy erection equipment is expected, provide a 200–300 mm Granular Sub-Base (GSB) over compacted subgrade.

 Ensure proper surface drainage to avoid saturation around tower foundations.

 Avoid prolonged water accumulation during monsoon by providing side drains and cross-fall on temporary access tracks.

 After excavation for tower foundations, remove any loose or softened material before placing PCC or concrete.

# 5. EARTH RESISTIVITY

Basis of Estimation:

Earth resistivity (ρ) depends primarily on:

• Soil type
• Moisture content
• Bulk density
• Clay percentage
• Degree of compaction

The proposed transmission line location at Nirona, Bhuj (Kutch) generally consists of:

- Medium stiff silty clay in the upper layer

- Dense sandy murum below 1.0 m depth

- Semi-arid climatic conditions

- Low natural moisture content

- No groundwater encountered within the preliminary investigation depth (2.0 m)

These conditions generally produce moderate to moderately high earth resistivity, particularly during the dry season.

5.1 Correlation Method (IS 3043 : 1998 – Wenner Method)

5.1 Correlation Method (IS 3043 : 1998 – Wenner Method)
ρ = 2π × a × R
where ρ = apparent resistivity (Ω·m), a = electrode spacing (m), R = field resistance (Ω)

5.2 Sample Calculation (Layer 1–2 m, SM murum)
Assumed field reading: a = 2 m, R = 10.11 Ω
ρ = 2 × 3.142 × 2 × 10.11 = 127.0 Ω·m

5.3 Estimated Resistivity by Layer:
0–1 m (CI-CL) : 50–60 Ω·m
1–2 m (SM)     : 80–90 Ω·m
Adopted design resistivity (dry season, conservative) = 85 Ω·m
Target earth resistance ≤ 10 Ω (substation / tower earthing)

Where:

Soil Behaviour Influence on Resistivity:

| Soil Parameter | Effect on Resistivity |
| --- | --- |
| Clay content increases | Resistivity decreases (more conductive path) |
| Moisture content increases | Resistivity decreases significantly |
| Sand / Murum content increases | Resistivity increases |
| Density / compaction increases | Resistivity increases under dry condition |

In this project:

 Upper layer consists of cohesive silty clay (moderate resistivity)

 Lower layer consists of dense sandy murum (higher resistivity)

 Semi-arid climate causes seasonal drying

 Groundwater not encountered within 2.0 m

Adopted Soil Parameters (From Soil Summary):

| Depth (m) | Soil Type | Bulk Density (g/cc) | Moisture Condition |
| --- | --- | --- | --- |
| 0–1 | CI – Medium Stiff Silty Clay | 1.90 | Moderate |
| 1–2 | SM – Dense Sandy Murum | 2.00 | Dry to Moderate |

Sample Calculation (1–2 m Depth):

Layer: SM  (Dense sandy murum)
Bulk Density (γ) = 2.00 g/cc
Moisture Condition = Dry to Moderate
Soil Type = Dense Granular Murum

Typical empirical resistivity range for dense sandy murum under semi-arid conditions:

Considering:

 No groundwater encountered

 Semi-arid regional climate

 Dry granular soil

 Low natural moisture

Dense compacted murum Applying dry-season correction factor (+10%):

Rounded practical design range:

Estimated Resistivity by Layer:

| Depth (m) | Soil Type | Estimated Resistivity (Ω·m) |
| --- | --- | --- |
| 0–1 | CI- Medium stiff Silty Clay | 50-60 |
| 1–2 | SM- Dense Sandy Murum | 80-90 |

Seasonal Variation:

- During monsoon → Resistivity may decrease by 20–35%

- During peak summer → Resistivity increases due to drying of the upper soil layers.

- Long-term design should consider dry-season resistivity.

- Upper clay layer may crack during extreme summer, resulting in localized increase in resistivity.

Therefore, a conservative upper-bound value is adopted for design.

Final Adopted Design Resistivity:

Earth Resistivity Conclusion:

| Parameter | Value |
| --- | --- |
| Estimated Resistivity | 50-90 Ω·m |
| Adopted Design Resistivity | 85 Ω·m |
| Earthing Type | Copper-bonded GI Pipe Earthing with interconnected grounding conductor |
| Recommended Pit Depth | 3.0 m |
| Target Earth Resistance | ≤ 10 Ohm (Substation) |
| Backfill Material | Bentonite-based conductive compound (or Charcoal + Salt where specified) |
| Seasonal Variation | 20-35% reduction during monsoon |